## Branch
From Number | From Name | To Number | To Name | From Area Name | To Area Name | From Nom kV | To Nom kV | Circuit | Status | Branch Device Type | Xfrmr | R | X | B | Lim MVA A | Lim MVA B | Lim MVA C
30005 | ROUND MT | 30065 | RD MT 1M | PG AND E | PG AND E | 500 | 500 | 1 | Closed | TransformerWinding | YES | 6e-05 | 0.01275 | 0 | 0 | 0 | 0
300003 | MN_RM_12 | 30005 | ROUND MT | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0072 | 0 | 2309 | 3464 | 2309
300006 | MN_RM_23 | 30005 | ROUND MT | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Series Cap | NO | 0 | -0.0072 | 0 | 2309.7 | 3464.1 | 2309.7
30005 | ROUND MT | 300051 | RM_TM_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.00832 | 0 | 1905.2 | 2840.5 | 2309.6
30005 | ROUND MT | 300053 | RM_TM_21 | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Series Cap | NO | 0 | -0.00832 | 0 | 1905.2 | 2840.5 | 2309.6
30015 | TABLE MTN | 30066 | TABLE MTN5M | PG AND E | PG AND E | 500 | 500 | 5 | Closed | TransformerWinding | YES | 7e-05 | 0.01367 | 0 | 1122 | 1122 | 1122
300052 | RM_TM_12 | 30015 | TABLE MTN | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.00832 | 0 | 1905.2 | 2840.5 | 2309.6
300054 | RM_TM_22 | 30015 | TABLE MTN | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Series Cap | NO | 0 | -0.00832 | 0 | 1905.2 | 2840.5 | 2309.6
30015 | TABLE MTN | 300151 | TM_VD_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0072 | 0 | 2145.9 | 3464 | 2309.6
30015 | TABLE MTN | 300153 | TM_TS_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0112 | 0 | 1931.2 | 3079.5 | 2309.6
300001 | CJ_OL_13 | 30020 | OLINDA | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.01 | 0 | 2338 | 3551 | 2338
30020 | OLINDA | 300201 | OL_MX_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.01 | 0 | 2468 | 3724 | 2468
300202 | OL_MX_12 | 30025 | MAXWELL | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0108 | 0 | 2468 | 3724 | 2468
30025 | MAXWELL | 300251 | MX_TR_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00082 | 0.02119 | 1.9842 | 2598 | 3897 | 2468
300152 | TM_VD_12 | 30030 | VACA-DIX | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0072 | 0 | 2145.9 | 3464 | 2309.6
30030 | VACA-DIX | 300301 | VD_TS_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0108 | 0 | 1931.2 | 2566.8 | 2309.6
30035 | TRACY | 30040 | TESLA | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0005 | 0.00166 | 0.16026 | 1931.2 | 3079.5 | 2987
30035 | TRACY | 30050 | LOSBANOS | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00068 | 0.01585 | 1.1513 | 1931.2 | 3079.5 | 2987
30035 | TRACY | 37508 | TCY MP1 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | TransformerWinding | YES | 2e-05 | 0.00583 | 0 | 850 | 1041 | 850
30035 | TRACY | 37510 | TCY MP2 | PG AND E | PG AND E | 500 | 500 | 2 | Closed | TransformerWinding | YES | 2e-05 | 0.00583 | 0 | 850 | 1041 | 850
300251 | MX_TR_11 | 30035 | TRACY | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0092 | 0 | 2468 | 3724 | 2468
30040 | TESLA | 30042 | METCALF | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0005 | 0.00881 | 0.59878 | 1931.2 | 3079.5 | 2598
30040 | TESLA | 30050 | LOSBANOS | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00059 | 0.01407 | 0.9944 | 1931.2 | 3079.5 | 2598
300154 | TM_TS_12 | 30040 | TESLA | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0112 | 0 | 1931.2 | 3079.5 | 2309.6
300301 | VD_TS_11 | 30040 | TESLA | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00059 | 0.01439 | 0.97812 | 1931.2 | 3079.5 | 2598
30042 | METCALF | 30045 | MOSSLAND | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0005 | 0.00888 | 0.60341 | 1931.2 | 3079.5 | 2598
30045 | MOSSLAND | 30050 | LOSBANOS | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00053 | 0.01297 | 0.88119 | 1931.2 | 3079.5 | 2598
366700 | DALLASES | 30045 | MOSSLAND | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 1e-05 | 0.00031 | 0.00691 | 850 | 850 | 850
30050 | LOSBANOS | 30055 | GATES | PG AND E | PG AND E | 500 | 500 | 3 | Closed | Line | NO | 0.00077 | 0.01855 | 1.5853 | 1931.2 | 3079.5 | 3431.1
30050 | LOSBANOS | 30069 | L.BANS M | PG AND E | PG AND E | 500 | 500 | 1 | Closed | TransformerWinding | YES | 6e-05 | -0.00275 | 0 | 0 | 0 | 0
30050 | LOSBANOS | 300501 | LB_GT_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0008 | 0.0199 | 1.4024 | 1931.2 | 3079.5 | 3431.1
30050 | LOSBANOS | 300502 | LB_MW_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0008 | 0.0199 | 1.4024 | 1931.2 | 3079.5 | 3431.1
30055 | GATES | 30057 | DIABLOCNYNSS | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00082 | 0.02015 | 1.3516 | 1931.2 | 2598 | 2598
300501 | LB_GT_11 | 30055 | GATES | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.01094 | 0 | 1931.2 | 3079.5 | 2309.6
30055 | GATES | 300551 | GT_MW_11 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0102 | 0 | 1931.2 | 3079.5 | 2309.6
30057 | DIABLOCNYNSS | 30060 | MIDWAY | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Line | NO | 0.00087 | 0.02107 | 1.441 | 1931.2 | 3079.5 | 3431.1
30057 | DIABLOCNYNSS | 30060 | MIDWAY | PG AND E | PG AND E | 500 | 500 | 3 | Closed | Line | NO | 0.00087 | 0.02117 | 1.4479 | 1931.2 | 3079.5 | 3431.1
300504 | LB_MW_13 | 30060 | MIDWAY | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0007 | 0.0157 | 1.109 | 1931.2 | 3079.5 | 2598
300551 | GT_MW_11 | 30060 | MIDWAY | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0007 | 0.0157 | 1.109 | 1931.2 | 3308 | 3431
40687 | MALIN | 300002 | MN_RM_11 | NORTHWEST | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.00716 | 0 | 2309.6 | 3464 | 2309.6
40687 | MALIN | 300004 | MN_RM_21 | NORTHWEST | PG AND E | 500 | 500 | 2 | Closed | Series Cap | NO | 0 | -0.00864 | 0 | 2310 | 3464 | 2310
450352 | CJ_OL_12 | 300001 | CJ_OL_13 | NORTHWEST | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00105 | 0.03087 | 2.8419 | 2598 | 3897 | 2598
300002 | MN_RM_11 | 300003 | MN_RM_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00103 | 0.02338 | 1.58 | 1931 | 3043 | 2598
300004 | MN_RM_21 | 300005 | MN_RM_22 | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Line | NO | 0.00055 | 0.01235 | 0.7635 | 2402 | 2678 | 3547
300005 | MN_RM_22 | 300006 | MN_RM_23 | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Line | NO | 0.00055 | 0.01235 | 0.7635 | 1905.2 | 2840.5 | 3166.1
300051 | RM_TM_11 | 300052 | RM_TM_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00108 | 0.02255 | 1.5085 | 1905.2 | 2841 | 2598
300053 | RM_TM_21 | 300054 | RM_TM_22 | PG AND E | PG AND E | 500 | 500 | 2 | Closed | Line | NO | 0.00107 | 0.0225 | 1.4997 | 1905.2 | 2841 | 2598
300151 | TM_VD_11 | 300152 | TM_VD_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00086 | 0.02104 | 1.4295 | 2145.9 | 3464 | 2598
300153 | TM_TS_11 | 300154 | TM_TS_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.0014 | 0.03412 | 2.3183 | 1931.2 | 3079.5 | 3167.8
300201 | OL_MX_11 | 300202 | OL_MX_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Line | NO | 0.00076 | 0.01952 | 1.8245 | 2598 | 3897 | 2598
300502 | LB_MW_11 | 300503 | LB_MW_12 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.01094 | 0 | 2309.7 | 3464.1 | 2309.7
300503 | LB_MW_12 | 300504 | LB_MW_13 | PG AND E | PG AND E | 500 | 500 | 1 | Closed | Series Cap | NO | 0 | -0.0102 | 0 | 2309.7 | 3464.1 | 2309.7

## Bus
Number | Name | Labels All | Area Name | Nom kV | PU Volt | Volt (kV) | Angle (Deg) | Load MW | Load Mvar | Gen MW | Gen Mvar | Switched Shunts Mvar | Act G Shunt MW | Act B Shunt Mvar | Area Num | Zone Num
300006 | MN_RM_23 |  | PG AND E | 500 | 1.0876 | 543.792 | -23.44 | [5 empty] | 0 | 0 | 30 | 300
300001 | CJ_OL_13 |  | PG AND E | 500 | 1.0871 | 543.552 | -28.31 | [5 empty] | 0 | 0 | 30 | 300
300002 | MN_RM_11 |  | PG AND E | 500 | 1.086 | 542.99 | -9.33 | [5 empty] | 0 | 0 | 30 | 300
300504 | LB_MW_13 |  | PG AND E | 500 | 1.0832 | 541.585 | -29.36 | [5 empty] | 0 | 0 | 30 | 300
300251 | MX_TR_11 |  | PG AND E | 500 | 1.0806 | 540.292 | -38.02 | [5 empty] | 0 | 0 | 30 | 300
300202 | OL_MX_12 |  | PG AND E | 500 | 1.0793 | 539.651 | -29.5 | [5 empty] | 0 | 0 | 30 | 300
300005 | MN_RM_22 |  | PG AND E | 500 | 1.0764 | 538.2 | -15.89 | [5 empty] | 0 | 0 | 30 | 300
300503 | LB_MW_12 |  | PG AND E | 500 | 1.0759 | 537.973 | -28.87 | [5 empty] | 0 | 0 | 30 | 300
300152 | TM_VD_12 |  | PG AND E | 500 | 1.0741 | 537.043 | -36.38 | [5 empty] | 0 | 0 | 30 | 300
300004 | MN_RM_21 |  | PG AND E | 500 | 1.0741 | 537.036 | -8.23 | [5 empty] | 0 | 0 | 30 | 300
300054 | RM_TM_22 |  | PG AND E | 500 | 1.0718 | 535.912 | -29.43 | [5 empty] | 0 | 0 | 30 | 300
300052 | RM_TM_12 |  | PG AND E | 500 | 1.0716 | 535.791 | -29.38 | [5 empty] | 0 | 0 | 30 | 300
300502 | LB_MW_11 |  | PG AND E | 500 | 1.0683 | 534.144 | -28.33 | [5 empty] | 0 | 0 | 30 | 300
300201 | OL_MX_11 |  | PG AND E | 500 | 1.068 | 533.998 | -13.48 | [5 empty] | 0 | 0 | 30 | 300
30035 | TRACY |  | PG AND E | 500 | 1.0671 | 533.535 | -30.7 |  |  |  |  | 683.18 | 0 | 0 | 30 | 300
30055 | GATES |  | PG AND E | 500 | 1.067 | 533.506 | -27.17 | [5 empty] | 0 | 0 | 30 | 300
300154 | TM_TS_12 |  | PG AND E | 500 | 1.0668 | 533.401 | -38.31 | [5 empty] | 0 | 0 | 30 | 300
30025 | MAXWELL |  | PG AND E | 500 | 1.0668 | 533.374 | -20.78 | [5 empty] | 0 | 0 | 30 | 300
30050 | LOSBANOS |  | PG AND E | 500 | 1.0667 | 533.325 | -29.31 | [5 empty] | 0 | 0 | 30 | 300
30005 | ROUND MT |  | PG AND E | 500 | 1.0654 | 532.678 | -19.04 | [5 empty] | 0 | 0 | 30 | 300
30060 | MIDWAY |  | PG AND E | 500 | 1.0633 | 531.651 | -28.54 | [5 empty] | 0 | 0 | 30 | 300
30057 | DIABLOCNYNSS |  | PG AND E | 500 | 1.0631 | 531.523 | -20.06 | [5 empty] | 0 | 0 | 30 | 300
300003 | MN_RM_12 |  | PG AND E | 500 | 1.0626 | 531.318 | -23.4 | [5 empty] | 0 | 0 | 30 | 300
300053 | RM_TM_21 |  | PG AND E | 500 | 1.0589 | 529.437 | -12.98 | [5 empty] | 0 | 0 | 30 | 300
30020 | OLINDA |  | PG AND E | 500 | 1.0588 | 529.412 | -21.79 |  |  |  |  | 224.22 | 0 | 0 | 30 | 300
300051 | RM_TM_11 |  | PG AND E | 500 | 1.0588 | 529.384 | -13.03 | [5 empty] | 0 | 0 | 30 | 300
30015 | TABLE MTN |  | PG AND E | 500 | 1.0582 | 529.087 | -23.48 |  |  |  |  | 0 | 0 | 0 | 30 | 300
300151 | TM_VD_11 |  | PG AND E | 500 | 1.0553 | 527.666 | -16.76 | [5 empty] | 0 | 0 | 30 | 300
30030 | VACA-DIX |  | PG AND E | 500 | 1.0542 | 527.086 | -29.85 | [5 empty] | 0 | 0 | 30 | 300
30040 | TESLA |  | PG AND E | 500 | 1.053 | 526.498 | -31.34 | [5 empty] | 0 | 0 | 30 | 300
300551 | GT_MW_11 |  | PG AND E | 500 | 1.0526 | 526.322 | -24.69 | [5 empty] | 0 | 0 | 30 | 300
300153 | TM_TS_11 |  | PG AND E | 500 | 1.0512 | 525.618 | -16.33 | [5 empty] | 0 | 0 | 30 | 300
300501 | LB_GT_11 |  | PG AND E | 500 | 1.0474 | 523.687 | -24.6 | [5 empty] | 0 | 0 | 30 | 300
30042 | METCALF |  | PG AND E | 500 | 1.0465 | 523.272 | -36.07 |  |  |  |  | 383.34 | 0 | 0 | 30 | 300
30045 | MOSSLAND |  | PG AND E | 500 | 1.0454 | 522.687 | -31.85 | [5 empty] | 0 | 0 | 30 | 300
366700 | DALLASES |  | PG AND E | 500 | 1.045 | 522.5 | -31.79 | [5 empty] | 0 | 0 | 30 | 319
300301 | VD_TS_11 |  | PG AND E | 500 | 1.0272 | 513.625 | -25.54 | [5 empty] | 0 | 0 | 30 | 300
30069 | L.BANS M |  | PG AND E | 500 | 1.0164 | 508.19 | -29.41 | [5 empty] | 0 | 0 | 30 | 300
37510 | TCY MP2 |  | PG AND E | 500 | 1.0145 | 507.251 | -32.03 | [5 empty] | 0 | 0 | 30 | 325
37508 | TCY MP1 |  | PG AND E | 500 | 1.0145 | 507.251 | -32.03 | [5 empty] | 0 | 0 | 30 | 325
30065 | RD MT 1M |  | PG AND E | 500 | 1.001 | 500.485 | -15.99 | [5 empty] | 0 | 0 | 30 | 300
30066 | TABLE MTN5M |  | PG AND E | 500 | 0.99595 | 497.974 | -21.62 | [5 empty] | 0 | 0 | 30 | 300